## Propuesta
PV System Calculator
A. Components | [5 empty] | Small fridge (example)
Qty. | Components | Watts | Hour/Day | Wh/dia | 20% Security Margin | Duty-Cycle Power Calculator
1 | Small fridge | 27 | 24 | 648 | 777.6 | power consumption | 2.57 | kWH
1 | Router #1 (HT2000W) | 75 | 10 | 750 | 900 | measurement hours | 96 | hr
0 | Component AC |  |  | 0 | 0 | actual wattage | 26.7708 | W
2 | Solar Tracking System (Max Load) | 36 | 0.5 | 36 | 43.2
2 | Solar Tracking System (No Load) | 10 | 1 | 20 | 24 | Duty-Cycle Power Calculator
1 | Fiber Optic Media Converter | 3 | 10 | 30 | 36 | For items (like fridges) that turn on and off
1 | Microcontroller | 0.25 | 3 | 0.75 | 0.9 | during the day, it's most accurate to
1 | LCD Display | 0.01 | 3 | 0.03 | 0.036 | measure KWH with a monitor device and
1 | Keyboard | 0.01 | 3 | 0.03 | 0.036 | calculate daily power consumption.
1 | USB Port #1 (Cellphone) | 6 | 6 | 36 | 43.2
0 |  |  |  | 0 | 0
|  | 157.27 |  | 1520.81 | 1824.972
B. Average day consumption | [5 empty] | F. Design Specification
Lmd DC |  | 43.2 | Wh/day |  |  | Minimum inverter wattage |  |  | 721.524 | W
Lmd AC |  | 1781.772 | Wh/day |  |  | Minimum battery AH reserve |  |  | 187.0126 | Ah
Battery efficency (Nbat) |  | 95 | % |  |  | Minimum solar panel modules |  |  | 1.3527 | Panels
Inverter efficency (Ninv) |  | 95 | % | [5 empty] | 1 | Serie
Conductor (Ncon) |  | 100 | % | [5 empty] | 1.3527 | Parallel
Battery voltage |  | 12 | V |  |  | Minimum charge contoller current |  |  | 45.4071 | A
Lmd |  | 2019.7363 | Wh/day
Qah |  | 168.3114 | Ah/day
C. Solar panels
Lmd |  | 2019.7363 | Wh/day
STC Wp |  | 300 | W
HPS |  | 5.53 | KW/m2
PR |  | 90 | %
Nt |  | 1.3527 | Modules
Battery voltage |  | 12 | V
STC Vmax |  | 37.46 | V
Nt |  | 1.3527 | Modules
Nserie |  | 1 | Modules
Nparalelo |  | 1.3527 | Modules
Corriente unitaria (Imod,mpp) |  | 8.01 | A
Corriente de cortocircuito( Imod,sc) |  | 9.56 | A
I(gfv, mpp) |  | 30.4361 | A
Nparalelo *Sin regulador MPPT |  | 3.7998 | Modules
D. Batterys
Descarga Max. Estacional |  | 90 | %
Descarga Max. diaria |  | 15 | %
Fct. |  | 1
Autonomy |  | 1 | dias
Cnd (Wh) |  | 18366.6667 | Wh
Cnd (Ah) |  | 1530.5556 | Ah
Cne (Wh) |  | 2244.1514 | Wh
Cne (Ah) |  | 187.0126 | Ah
E. Charge controller & inverter
IN current |  | 45.4071 | A
OUT current |  | 17.2116 | A
Power DC |  | 6 | W
Power AC |  | 151.27 | W
Inverter power (Pinv) |  | 181.524 | W
Power Inverter + surge fridge(Pinv) |  | 721.524 | W

## Prototipo
PV System Calculator
A. Components | [5 empty] | Small fridge (example)
Qty. | Components | Watts | Hour/Day | Wh/dia | 20% Security Margin | Duty-Cycle Power Calculator
1 | Router | 7.5 | 2 | 15 | 18 | power consumption | 2.57 | kWH
1 | Modem | 6 | 2 | 12 | 14.4 | measurement hours | 96 | hr
0 |  |  |  | 0 | 0 | actual wattage | 26.7708 | W
1 | Arduino Mega | 0.27 | 2 | 0.54 | 0.648
1 | Arduino UNO | 0.29 | 2 | 0.58 | 0.696 | Duty-Cycle Power Calculator
2 | Relays | 0.25 | 2 | 1 | 1.2 | For items (like fridges) that turn on and off
1 | LCD Keyboard Shield | 0.25 | 2 | 0.5 | 0.6 | during the day, it's most accurate to
1 | Stepper motor | 24 | 0.25 | 6 | 7.2 | measure KWH with a monitor device and
0 |  |  |  | 0 | 0 | calculate daily power consumption.
1 | Celular | 6 | 2 | 12 | 14.4
0 |  |  |  | 0 | 0
|  | 44.56 |  | 47.62 | 57.144
A. Average day consumption | [5 empty] | F. Design Specification
Lmd DC |  | 14.4 | Wh/day |  |  | Minimum inverter wattage |  |  | 46.272 | W
Lmd AC |  | 42.744 | Wh/day |  |  | Minimum battery AH reserve |  |  | 8.4036 | Ah
Battery efficency (Nbat) |  | 70 | % |  |  | Minimum solar panel modules |  |  | 0.82889 | Panels
Inverter efficency (Ninv) |  | 87 | % | [5 empty] | 1 | Serie
Conductor (Ncon) |  | 100 | % | [5 empty] | 0.82889 | Parallel
Battery voltage |  | 12 | V |  |  | Minimum charge contoller current |  |  | 1.7096 | A
Lmd |  | 90.7586 | Wh/day
Qah |  | 7.5632 | Ah/day
C. Solar panels
Lmd |  | 90.7586 | Wh/day
STC Wp |  | 22 | W
HPS |  | 5.53 | KW/m2
PR |  | 90 | %
Nt |  | 0.82889 | Modules
Battery voltage |  | 12 | V
STC Vmax |  | 18 | V
Nt |  | 0.82889 | Modules
Nserie |  | 1 | Modules
Nparalelo |  | 0.82889 | Modules
Corriente unitaria (Imod,mpp) |  | 1.3 | A
Corriente de cortocircuito( Imod,sc) |  | 1.3 | A
I(gfv, mpp) |  | 1.3677 | A
Nparalelo *Sin regulador MPPT |  | 1.0521 | Modules
D. Batterys
Descarga Max. Estacional |  | 90 | %
Descarga Max. diaria |  | 15 | %
Fct. |  | 1
Autonomy |  | 1 | dias
Cnd (Wh) |  | 18366.6667 | Wh
Cnd (Ah) |  | 1530.5556 | Ah
Cne (Wh) |  | 100.8429 | Wh
Cne (Ah) |  | 8.4036 | Ah
E. Charge controller & inverter
IN current |  | 1.7096 | A
OUT current |  | 5.2419 | A
Power DC |  | 6 | W
Power AC |  | 38.56 | W
Inverter power (Pinv) |  | 46.272 | W
Power Inverter + surge fridge(Pinv) |  | 586.272 | W

## Eolica
Wind Turbine Power Generated Calculator | [18 empty] | Wind Turbine Performance
[19 empty] | Wind (MPH) | Watts (W)
Meses | Municipios | [17 empty] | 0 | 0
| Ponce |  | San Juan |  | Mayaguez |  | Arecibo |  | Fajardo |  | Caguas |  | Orocovis |  | Lares |  | Santa Isabel |  | 40 | 6
Enero | 11.5 | 217 | 11.8 | 217 | 12 | 217 | 11.5 | 217 | 12.2 | 217 | 11.5 | 217 | 11.2 | 150 | 11.2 | 150 | 11.8 | 217 | 47 | 7
Febrero | 11.5 | 217 | 11.8 | 217 | 11.8 | 217 | 11 | 150 | 12 | 217 | 11.5 | 217 | 11.2 | 150 | 11 | 150 | 11.8 | 217 | 53 | 8
Marzo | 11 | 150 | 11.2 | 150 | 11 | 150 | 10.5 | 150 | 11.5 | 217 | 11 | 150 | 10.8 | 150 | 10.5 | 150 | 11 | 150 | 60 | 9
Abril | 10.5 | 150 | 10.8 | 150 | 10.2 | 105 | 10 | 105 | 11 | 150 | 10.7 | 150 | 10.5 | 150 | 9.8 | 105 | 10.5 | 150 | 105 | 10
Mayo | 10.5 | 150 | 10.5 | 150 | 10.2 | 105 | 9.5 | 105 | 11 | 150 | 10.2 | 105 | 10.2 | 105 | 9.7 | 105 | 10.4 | 105 | 150 | 11
Junio | 11.5 | 217 | 11 | 150 | 11.8 | 217 | 11 | 150 | 12 | 217 | 11 | 150 | 11 | 150 | 11 | 150 | 11.8 | 217 | 217 | 12
Julio | 12.4 | 217 | 12.5 | 375 | 12.5 | 375 | 11.8 | 217 | 13 | 375 | 12.5 | 375 | 12.2 | 217 | 11.9 | 217 | 12.5 | 375 | 375 | 13
Agosto | 11.5 | 217 | 11 | 150 | 11.8 | 217 | 11 | 150 | 12 | 217 | 11 | 150 | 11 | 150 | 11 | 150 | 11.8 | 217 | 650 | 15
Septiembre | 9.5 | 105 | 10 | 105 | 10 | 105 | 9 | 60 | 10.2 | 105 | 10 | 105 | 9.7 | 105 | 9.2 | 60 | 10 | 105 | 750 | 17
Octubre | 9 | 60 | 9.3 | 60 | 9.3 | 60 | 8.7 | 60 | 9.7 | 105 | 9.2 | 60 | 8.9 | 60 | 8.7 | 60 | 9.1 | 60 | 900 | 20
Noviembre | 10.1 | 105 | 10.9 | 150 | 11 | 150 | 10.5 | 150 | 11 | 150 | 11 | 150 | 10.5 | 150 | 10.5 | 150 | 10.5 | 150 | 1100 | 22
Diciembre | 11.2 | 150 | 11.8 | 217 | 12 | 217 | 11 | 150 | 12.2 | 217 | 11.5 | 217 | 11 | 150 | 11.2 | 150 | 11 | 150 | 24 | 1200
| MPH | Watts | MPH | Watts | MPH | Watts | MPH | Watts | MPH | Watts | MPH | Watts | MPH | Watts | MPH | Watts | MPH | Watts | 26 | 1325
[19 empty] | 29 | 1450
[19 empty] | 32 | 1500
https://es.weatherspark.com/y/27814/Clima-promedio-en-San-Juan-Puerto-Rico-durante-todo-el-a%C3%B1o

## Teorico vs Medido
Consumo Teorico vs Medido
Current (A)
Components | Watts (W) | Voltage (V) | Calculated | Measured | Column1
Arduino Mega | 0.27 | 9 | 0.03 | .093 A
Arduino UNO | 0.29 | 9 | 0.032222 | .046 A
Relay x2 | 0.35 | 5 | 0.07 | .14 A | 15-20mA
Stepper Motor | 2 |  | #DIV/0! | 2.0 A |  |  | 0.35
ARRIS TG862A Modem | 0.7 |  | #DIV/0! | .7 A |  | 0.1
Linksys E1000 Router | 0.5 |  | #DIV/0! | .5 A